## Risk Register_ Phase
Check box if it is a Risk. | Row ID | Risk Category | Short Tile | Definition (What is the Risk?) | What is the Cause? | What is the Impact? | Mitigation Plan | Risk Review Comments | Risk Owner (Responsible) | Status | Probability [1-Low/5 Certain] | Impact [1-Low/5 Critical] | Severity | Priority | Cost Impact Score | Budget Impact | Cost Impact Matrix 1 | Cost Impact Matrix 2 | Date of Resolution | Progress Update | Progress Updated Tracking | Date Closed
| SD001 | [8 empty] | Closed |  |  | 0 |  |  |  | 1-1 | 10000 |  |  | 2024-05-08 16:54
| SD002 | [8 empty] | Closed |  |  | 0 |  |  |  | 1-2 | 30000 |  |  | 2024-05-08 16:54
| SD003 | [8 empty] | Closed |  |  | 0 |  |  |  | 1-3 | 50000 |  |  | 2024-05-08 16:54
| SD004 | [8 empty] | Closed |  |  | 0 |  |  |  | 1-4 | 100000 |  |  | 2024-05-08 16:54
| SD005 | [8 empty] | Closed |  |  | 0 |  |  |  | 1-5 | 200000 |  |  | 2024-05-08 16:54
| SD006 | [8 empty] | Closed |  |  | 0 |  |  |  | 2-1 | 60000 |  |  | 2024-05-08 16:54
| SD007 | [8 empty] | Closed |  |  | 0 |  |  |  | 2-2 | 100000 |  |  | 2024-05-08 16:54
| SD008 | [8 empty] | Closed |  |  | 0 |  |  |  | 2-3 | 200000 |  |  | 2024-05-08 16:54
| SD009 | [8 empty] | Closed |  |  | 0 |  |  |  | 2-4 | 400000 |  |  | 2024-05-08 16:54
| SD010 | [8 empty] | Closed |  |  | 0 |  |  |  | 2-5 | 800000 |  |  | 2024-05-08 16:54
| SD011 | [8 empty] | Closed |  |  | 0 |  |  |  | 3-1 | 150000 |  |  | 2024-05-08 16:54
| SD012 | [8 empty] | Closed |  |  | 0 |  |  |  | 3-2 | 300000 |  |  | 2024-05-08 16:54
| SD013 | [8 empty] | Closed |  |  | 0 |  |  |  | 3-3 | 600000 |  |  | 2024-05-08 16:54
| SD014 | [8 empty] | Closed |  |  | 0 |  |  |  | 3-4 | 1200000 |  |  | 2024-05-08 16:54
| SD015 | [8 empty] | Closed |  |  | 0 |  |  |  | 3-5 | 1800000 |  |  | 2024-05-08 16:54
| SD016 | [8 empty] | Closed |  |  | 0 |  |  |  | 4-1 | 400000 |  |  | 2024-05-08 16:54
| SD017 | [8 empty] | Closed |  |  | 0 |  |  |  | 4-2 | 800000 |  |  | 2024-05-08 16:54
| SD018 | [8 empty] | Closed |  |  | 0 |  |  |  | 4-3 | 1600000 |  |  | 2024-05-08 16:54
| SD019 | [8 empty] | Closed |  |  | 0 |  |  |  | 4-4 | 2400000 |  |  | 2024-05-08 16:54
| SD020 | [8 empty] | Closed |  |  | 0 |  |  |  | 4-5 | 3200000 |  |  | 2024-05-08 16:54
| SD021 | [8 empty] | Closed |  |  | 0 |  |  |  | 5-1 | 1000000 |  |  | 2024-05-08 16:54
| SD022 | [8 empty] | Closed |  |  | 0 |  |  |  | 5-2 | 2000000 |  |  | 2024-05-08 16:54
| SD023 | [8 empty] | Closed |  |  | 0 |  |  |  | 5-3 | 3000000 |  |  | 2024-05-08 16:54
| SD024 | [8 empty] | Closed |  |  | 0 |  |  |  | 5-4 | 4000000 |  |  | 2024-05-08 16:54
| SD025 | [8 empty] | Closed |  |  | 0 |  |  |  | 5-5 | 5000000 |  |  | 2024-05-08 16:54
| SD0013 | External | Police Interface - response system required | Implementing and maintaining a system that meets stringent response and hardening requirements. | If we have alarming at a classified level, this may be requested to meet response requirements (5 or 15 minutes). If 15 minutes, additional hardening is typically required. | Additional hardening can increase both the complexity and the cost of the security infrastructure. Enhancing system robustness through hardening might increase initial costs by 20-30%. This includes upgrades to physical and cybersecurity systems, installation of redundant systems, and advanced surveillance technologies. | Cost Savings suggestions: Implement AI-driven surveillance and automated systems to reduce the need for large human response teams and decrease reaction time. This would be done in reduction in human surveillance labor costs by approximately 20-40% of the total increase. - Need to identify Levels | Classified storage onsite, Meeting on Monday to bring to discussions, right around 6-7 layers | mhankewycz@m2hprotection.com | At Risk | 2 | 2 | 4 | P1 | 3 | 300000 |  |  |  |  | 2024-05-22 07:49
| SD0014 | External | Water Availability | Water availability given allowances for additional ACM site development. If this is a single point of failure, then this would be an outage to our facility since there is no redundant feed. | Utility capacity and planning for ACM site development. | Critical for cooling capacity, feed up to max 140 MW, could create outage to site | 650K/day need, need to clarify with Utility - Once public, ask AHJ to lock in capacity for our site. Start Conversations with ACM now. | According to "available" allowance on past historical supply to the site meets the need. If some of that supply is shared then we are at risk of not meeting needs. | jamison.caldwell@smithgroup.com | In Control | 2 | 3 | 6 | P2 | 3 | 300000 |  |  |  |  | 2024-05-22 07:49
| SD0018 | External | ACM Site Planning | As yet unknown future project requirements or allowances. |  |  |  |  | jamison.caldwell@smithgroup.com | Closed | 0 | 0 | 0 |  | 0 | #NO MATCH |  |  |  |  | 2024-06-07 14:18
| SD0019 | External | Natural Disaster: Dam Rupture | A prelimnary natural hazard review was performed. Data for that review is on file but generally found to be minimal. One potential issue is dam rupture. Flood maps in the study were for 25 years not 100 or 500 year. | Unmanaged dam rupture. 100 or 500 year floods should be reviewed. | 25 year data was low risk for impact. 100 and 500 year data is unknown. Could impact contamination to site | Reports from Dam from Army Corp of Engineers, obtain 100-500year data to confirm no updates to site | What about Motion tests for seismic? | mhankewycz@m2hprotection.com | At Risk | 1 | 2 | 2 | P1 | 2 | 60000 |  |  |  |  | 2024-05-22 07:49
| SD00112 | External | High Voltage (ITC) lines | High Voltage (ITC) lines can support up to 200MW, which may not be enough to support future ACM loads and additional Project L densification | Size of existing ITC overhead lines | ITC lines would need to be upgraded in the future if >200MW is needed at the site. | LANL gave us worse case scenario, if ACM brings in another client to site, ITC Lines could be upgraded | Only leaves 40 for ACM | andrew.varilone@smithgroup.com | In Control | 1 | 1 | 1 | P1 | 1 | 10000 |  |  |  |  | 2024-05-22 07:49
| SD00120 | External | FAA - Height Restrictions | Mechanical Room Heights limitations, lower foundations | There are building height restrictions in certain areas of the property relative to the runway protection zones (not applicable to project L) and other zoned areas (applicable to Project L). See FAA and WCAA zoning and ordinance documents. Airport Zoning Authority has zoned the project L site Zone B which extends for a 3 mile radius around the Willow Run Airport. For Zone B, a permit shall be required for new construction and alterations to structures and objects exceeding airport elevation by 50'. The established airport elevation for Willow Run Airport is 716 AMSL (feet above mean sea level). Structures shall not exceed elevation 766 feet AMSL without a permit from the Airport Zoning Authority | Mechanical Room Heights and Construction Crane Heights - Long Permit for FAA Approvals - Foundations lowered and civil will need to be modified - Fall restraints required with lower parapets | - Ask for permit from FAA to be above 50' (Owner not interested in getting waiver) - Lower Mechanical Room Heights. - Alternate fall restraints system - cost impact - Lower parapet heights | GM building appears high, elevation confirmed heights at 802' and 834' for stacks (This exceeds our needs) We are roughly 3-1/2' above 716' | chris.devick@smithgroup.com, jamison.caldwell@smithgroup.com, jason.smith@smithgroup.com, Laura Holman, Marty Sterr, paul.locher@smithgroup.com | At Risk | 3 | 2 | 6 | P2 | 2 | 200000 |  |  |  |  | 2024-05-22 09:59
| SD00133 | Mechanical | Densities up to 1MW per HPC | Can only plan on densities up to 1MW per HPC; need to set limits on densification potential. | - Cooling Efficiency: higher density generates more heat - local power grid capabilities restricting how much power can be effectively supplied to each single cluster - The current state of server and cooling technology may not efficiently support higher densities for HPC workloads without significant compromises in reliability and performance | - Drives up space requirements to accommodate 100 separate clusters, influences the size and layout of data center, increasing the footprint to accommodate these distinct clusters while maintaining airflow and cooling paths. - Complicates power infrastructure and drives robust PDUs and is driving more substations or power feed needs to ensure the reliable power delivery to each cluster. - Drives more advanced cooling solutions to manage the heat effectively without allowing hot spots that would impact equipment performance. - More complex networking, requires high bandwidth and low latency connections across broader area and drives up the need to incorporate more fiber runs and switches - Drives higher construction and operational costs due to increase use of land, more complex infrastructure, and higher maintenance requirements. | - Energy efficient power supplies - Liquid cooling technology - Modular design - Secondary plant within the Modular design - Use virtualization and container technologies to maximize hardware utilization. This approach allows multiple virtual machines or containers to run on a single server, effectively increasing the compute density without physically adding more hardware. - Design clusters to share certain resources like storage or networking infrastructure to reduce redundancy and the associated costs. - Optimize the network layout and switch configuration to reduce cabling, switch counts, and overall complexity, which can lead to significant cost savings in both materials and ongoing maintenance. | Can't put more than 8 MW in a row (4 throughout recommended) | jamison.caldwell@smithgroup.com | In Control | 2 | 3 | 6 | P2 | 3 | 300000 |  |  |  |  | 2024-05-22 07:49
| SD00137 | Civil | Rainwater | Space for Rainwater treatment skid | Sustainability concept requirement | - Space Requirements that will impact reducing space allocated for other functions or expanding DC footprint - Weight of Water treatment system (full of water) could require additional structural support - Impacts plumbing scope to collect, treat, and reuse or dispose of water (need to watch out that this doesn't impact critical power and data infrastructure) - Require easy access to maintenance so not to disrupt the data center operations or security | - Environmental impact assessments to understand all potential sustainability needs and water management - possible integration with other water systems, like cooling systems? - Opportunity of a masterplan and support Sustainability, 100% offset flushing demand | Currently budget carried specifically for this, need to vet this out and get the recommended storm/rain water management. | jamison.caldwell@smithgroup.com | In Control | 3 | 2 | 6 | P2 | 2 | 200000 |  |  |  |  | 2024-05-13 09:41
| SD00138 | Civil | Depth of Condenser WaterLines | Depth of condenser water lines across site has not yet been extensively coordinated. | Not well documented, | - Construction Delays if Depth isn't identified correctly - Increase Cost - Impact Cooling system efficiency if not properly installed condenser lines (lines too shallow drive temp fluctuations and too deep drive increase energy cost - Risk of Damage | - Close coordination with Design Team internally - GPR Technology | want more space in mechanical room until we know more about condenser lines | jamison.caldwell@smithgroup.com | At Risk | 2 | 3 | 6 | P2 | 3 | 300000 |  |  |  |  | 2024-05-22 07:49
| SD00140 | Mechanical | Has the cooling system selected taken into account local climate extremes so that we can document the need to design at 0.4% condition but plan on capacity at the 50 yr condition. | Water quality testing has not been performed. Air quality should pose minimal risk since limited air-side economization. | brownfield site where contamination from past industrial activities could affect groundwater or surface water. | - Special treatment requirements - Chemical Treatment | - Environmental assessment to determine water treatment options - Upgrade to Carbon or HEPA filters Expectation management | Have we confirmed Discharge capacity by City and Water Pressure meetings design needs? Low risk on Air quality due to air-side economization still could be risky even in limited use, without an air quality test, how do we know as data centers do require cleanroom status. - Based on Site Study Notes: Water quality testing from each of the water treatment plants is available for 2021 and 2022. Following up with YCUA to see if 2023 data has been made public. Further discussion of water quality can be directed to YCUA Water Distribution staff. | jamison.caldwell@smithgroup.com | At Risk | 1 | 3 | 3 | P1 | 3 | 150000 |  |  |  |  | 2024-05-22 07:49
| SD031 | Mechanical | Yard Space for Equipment | Increase space needs in yard for Day 1 Equipment | Limit future Capacity | May limit availability of space for future Equipment needs. | Expectation Management |  | jamison.caldwell@smithgroup.com | In Control | 5 | 1 | 5 | P2 | 1 | 200000 |  |  |  |  | 2024-05-22 07:49
| SD026 | Mechanical | System Complexity & Integration Challenges | System Complexity: Multiple systems interplaying might pose challenges during commissioning or during unforeseen scenarios, | Multiple Systems interplaying | can lead to integration challenges during both installation and operation. | phased testing and commissioning processes, and robust integration protocols can help ensure that all systems function as intended when working together. Write into MEP Specs to provide Cx assist. Strong Recommendation for Owner, Cx agent 3rd party hired through SG (work with clients to write this into the scope) | May want to require this as part of Commissioning requirements to ensure we are not caught with this as a change order and no longer within a competitive nature. | Brandon Stanley | At Risk | 4 | 3 | 12 | P3 | 3 | 1200000 |  |  |  |  | 2024-05-22 07:49
| SD032 | Security | LANL Security Risk Assessment | Receivng guidance on security risk after critical decisions need to be made. | Alignment of LANL Security risk assessment timeframe with project schedule. | - Redesign and retrofitting costs - Project Delays - Compromised security posture that could be impossible to mitigate if construction is underway - drives late changes and cost/schedule impacts | - Designing conservative ahead of understanding the critical decisions from LANL - Keep site fencing as an alternate and be sure to track space for the fence - Utility yard will be fenced. | What specifically are the Major Changes? - Site Stand-off (minimal) - Fencing around facility not required - not finalized - Vehicle access control will occur and vehicle screening will happen off-site with ACM (This is still pending) Should maintain man Guard shack and man controls | mhankewycz@m2hprotection.com | At Risk | 3 | 1 | 3 | P1 | 1 | 50000 |  |  |  |  | 2024-05-22 07:49
| SD033 | Mechanical | Vapor drift studies to the airport | Cooling Towers Vapor Drift | Cooling towers used in data centers emit water vapor as a byproduct. This vapor, under certain meteorological conditions, can drift over long distances | - Airport: vapor plumes can reduce visibility or even lead to icing conditions in cold weather - Air traffic safety - Could drive regulatory implications of fines or mandatory changes to HPC Operations - Public Safety and HPC reputation | - Vapor Drift Studies - drift eliminators - Positioning Cooling Towers in a way that prevailing winds direct vapor away from Airport |  | jamison.caldwell@smithgroup.com | In Control | 2 | 1 | 2 | P1 | 1 | 30000 |  |  |  |  | 2024-05-22 07:49
| SD034 | Sustainability | Source carbon utilization | Project carbon goals are based on forecast for MI electric grid that has a favorable mid-term forecast for renewables. | Dependence on Regional Grid Forecasts | - Purchase Carbon Credits - Consuming more fossil fuel-based power than anticipated | - On site renewable energy - Energy Storage Systems | MU will need to own this | jamison.caldwell@smithgroup.com | At Risk | 1 | 1 | 1 | P1 | 1 | 10000 |  |  |  |  | 2024-05-22 07:49
| SD035 | External | Complex regulatory environment | ACM approval is required but does not have overall approval for site that would forego other required approvals. | The Township Planning Commission (inclusive of Roads Drainage Commission, other), WRAD, and potentially RACER, EGLE and FAA may have to approve aspects of the project. | - Any one of these approvals can delay project - Differing regulatory bodies may have differing requirements that drive scope changes, cost impacts, etc. - High Risk of over-looking requirements | - Early engagement with all regulatory involved - Engage someone who sole focus is to coordinate the differing regulatory requirements and tracking their integration (QAQC) | Needs to track until have coordination is complete | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | At Risk | 3 | 2 | 6 | P2 | 2 | 200000 |  |  |  |  | 2024-05-31 13:11
| SD038 | Sustainability | Hydrogen Plant Availability | Uncertainty in Hydrogen Production Timing and Development | - Is there Dependence on availability of locally produced hydrogen? - Lack of control over timeline | - lowers cost - reconfigures building closer to utility yard. - Better security - Cost associated with buying more land - MORE WORK, added scope | Opportunity if it is available that will allow mechanical yard closer to facility and lowers the cost. | ACM Comment: The BayoTech hydrogen production timing is still TBD but likely late 2026 if it moved forward to build out. There are other hydrogen programs including a U.S. DOE H2 Hub and other commercial H2 projects under consideration. These however be located on other parts of the property. | andrew.varilone@smithgroup.com, brian.rener@smithgroup.com, chris.devick@smithgroup.com, dino.lekas@smithgroup.com, jamison.caldwell@smithgroup.com, jason.smith@smithgroup.com, Laura Holman, Marty Sterr | In Control | 2 | 3 | 6 | P2 | 3 | 300000 |  |  |  |  | 2024-05-31 08:00
| SD039 | Civil | Utility Restrictions and Relocation Necessities | The main risk is that the development of the HPC DC might face restrictions or complications due to utility lines, particularly stormwater drains, that need to run through or around the hydrogen plant site. | - Proximity to Hydrogen Plant: The HPC data center is planned near a hydrogen plant, which can be a highly sensitive area due to the explosive and flammable nature of hydrogen. This proximity introduces restrictions on what can be built or routed through the area, including utilities. - Existing Infrastructure Layout: The existing storm sewer that drains the property is located east of the hydrogen plant, implying that new development (including the data center) may need to reroute or extend existing piping systems to connect to the public storm sewer system, which is not currently integrated. | - Design and Planning Delays - Increased Costs: Moving utilities, particularly large infrastructure like storm sewers, can be costly. There may be additional expenses related to engineering studies, construction, and potential disruption of other services. - Operational Constraints: Restrictions on where utilities can be placed may limit design options for the data center or require compromises in terms of layout and functionality. - Compliance and Safety Concerns: Working near a hydrogen plant requires adherence to stricter safety and compliance guidelines, which can complicate construction and operational practices. | ACM Comment: Some of this work was planned to be completed before the H2 plant went in and was intended to take into consideration the storm sewer connection to drain the entire property. We are looking at what an agnostic design might look like in the scenario where the H2 plant gets completed or in the case where Project L takes that parcel. | Keep this tracked due to the possibility of storm line change. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com, Rob Teifer | In Control | 1 | 2 | 2 | P1 | 2 | 60000 |  |  |  |  | 2024-06-07 14:24
| SD040 | Civil | Competition for Limited Utilities: The client wants to ensure that future development within the ACM property does not restrict the utility demands of the project. | The primary risk is the potential shortage or restriction of essential utilities (power, water, gas) due to shared demands among various projects on the ACM property, including the proving ground, test facilities, and future hydrogen production facilities. This could limit the availability of necessary resources for the HPC Data Center. | Insufficient Current Utility Data and Planning: There appears to be a lack of specific utility usage data and forward-looking utility capacity planning. This is compounded by challenges in obtaining clear, future-oriented answers from utility companies like DTE and other stakeholders like YUCA. Multiple Large-Scale Developments: Concurrent development projects on the ACM property, all requiring substantial utility inputs, increase the strain on available resources. | - Potential Delays in HPC Data Center Implementation: If utility demands exceed the current supply and enhancements to infrastructure are not timely, it could delay the commissioning of the HPC Data Center. - Increased Costs: Limited utility availability may lead to increased operational costs, including the need for the HPC project to invest in utility infrastructure upgrades or alternative solutions. - Restrictions on Future Expansion | Water is not a concern, no gas is a concern, but the unknown is ACM and they indicated they wouldn't Undermind this project associated with Utilities. Mostly a Power is the concern. | ACM Comment: We need to understand the utility demands of the project to better answer this question. We have not been provided any specifications of utility requirements and timeline. A forward looking plan needs to developed with the utilities to know what is available today and what will be available in the future with continued expansion and investment. DTE leadership needs to be engaged as we have been unable to get a forward looking answer from their account level team. YUCA also needs to be engaged. Our desired approach would be for the utilities to help define what is available and then develop a forward-looking plan to protect for utilities and real estate for our continued development. ACM intends to further develop its property which may require access to available utilities (power, gas, water). These projects include operation of our proving ground and test facilities (including higher power EV charging) and potential future green hydrogen production which will require power and water. There is going to be a minimum amount of power we must earmark for our operations and reasonable growth. However, our approach is to holistically plan available utilities for Project L and other planned efforts. | andrew.varilone@smithgroup.com, chris.devick@smithgroup.com, dino.lekas@smithgroup.com | In Control | 1 | 3 | 3 | P1 | 3 | 150000 |  |  |  |  | 2024-05-31 12:45
| SD041 | Civil | Incomplete Master Planning and Coordination | No Development or Planning Overlays exist | - Ongoing Planning Process: The master plan for the site is not yet complete, which means that decisions are currently being made without a comprehensive view of all future developments. - Lack of Comprehensive Development Overlays: Without existing overlays or fully defined plans that show how the site will be developed, there's a risk that new projects might not align with future site uses or township regulations. - Development Agreement Constraints: The existence of a development agreement between ACM and the Township might include stipulations that could impact the design, utility provisioning, and construction of Project L. | - Potential for Project Delays: Delays could occur if conflicts arise between the ongoing development of Project L and other projects due to a lack of integrated planning. - Increased Costs: Unforeseen conflicts with utilities, land use, or compliance with township agreements may necessitate design changes or infrastructure upgrades, leading to increased costs. - Regulatory and Compliance Issues: Failure to adhere to the terms of the development agreement or to meet township expectations could result in compliance issues, penalties, or forced alterations to the project. - Suboptimal Site Utilization: Without a comprehensive master plan, the site might not be used to its full potential, impacting the overall efficiency and effectiveness of the developments. | No development or planning overlays exist which would restrict project L site development. A devlopment agreement between ACM and the Township does exist. ACM to provide relevant information from that development agreement for Project L to understand township expectations of development on site. | ACM Comment: We are finalizing a Master Plan of the existing site to help us plan for future development but it does not yet show all future development. We maintain a trade space matrix of projects tracking real estate needs, location, power requirements, timeline, probability, to ensure we can foresee conflicts between projects. The best approach is to understand your requirements and timeline and develop a plan relative to available utilities and land. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 12:45
| SD046 | Civil | Compliance with Regulatory Stormwater Management Requirements - Will WRC require us to explore infiltrations. | Unknown if infiltration requirements will be applied. | - Environmental Restrictions: The site has environmental restrictions related to the management of stormwater, particularly regarding the infiltration and release of stormwater to public infrastructure. These restrictions are possibly due to underlying environmental sensitivities like soil composition, contamination, or proximity to protected ecosystems. - Regulatory Complexity: The involvement of multiple regulatory bodies (EGLE, RACER) and the need to follow specific environmental covenants increase the complexity of compliance and necessitate precise planning and coordination. | - Project Delays: Non-compliance with environmental regulations or failure to properly coordinate with regulatory bodies could lead to project delays, including stop-work orders or required redesigns of stormwater systems. - Increased Costs - Legal and Financial Liabilities | ACM suggested the Project L team engage RACER/EGLE to understand the stormwater management strategy that is preferred at the site, as it might be different than most site developments with respect to dentention and release of stormwater to the public infrastructure. Direct release of stormwater to the public infrastructure could be the preferred approach versus holding on site and controlling the rate of release. | 3/5/24 SO Comment: Section 4.0 Environmental: Yes, there are numerous environmental related restrictions that apply to this property (both the northern and southern). I am going to forward 2 restrictive covenants in a separate email to our workflow team that will be helpful to everyone. I recommend that everyone reviews these carefully, and then we can discuss and meet with EGLE after this. Any such meeting should also involve RACER and EHS. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | In Control | 1 | 3 | 3 | P1 | 3 | 150000 |  |  |  |  | 2024-05-31 12:50
| SD050 | Civil | Has the site survey/Light Detection and Ranging executed to verify topography cut & fill assumptions and calculate volume of material been completed? | RISK? |  |  |  | Preliminary survey data has been received |  | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:59
| SD051 | Civil | What steps are needed to gain permission for access and drilling? | RISK? |  |  |  | required approvals to proceed in process |  | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:59
| SD052 | Civil | Who locates utilities since this is private property? | RISK? |  |  |  | required approvals to proceed in process, survey completed |  | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:59
| SD053 | Civil | Insufficient Water Supply Capacity | The primary risk is that the existing water main system may not provide the required capacity for the HPC data center, particularly if the currently available data (flow test data) does not confirm the adequacy of the existing infrastructure. | - Existing Infrastructure Limitations: The 8-inch and 24-inch water mains might not have been designed to meet the high water demand of an HPC data center, which requires significant cooling and possibly fire suppression systems that consume a substantial amount of water. - Uncertainty in Data: Awaiting flow test data introduces a degree of uncertainty. Decisions or assumptions are being made without complete information, which can lead to planning based on incorrect assumptions about the infrastructure’s capacity. | - Project Delays: If it turns out that the existing water mains cannot support the required capacity, this could lead to delays in the project as additional planning, design, and construction work to upgrade the water mains would need to be carried out. - Increased Costs: Upgrading the water main system (upsizing pipes, for instance) to meet the needs of the data center would likely incur significant additional costs. This includes not only the physical work of replacing or augmenting pipes but also the costs associated with extended project timelines. - Operational Inefficiencies: In a scenario where the water supply is insufficient and cannot be quickly resolved, the data center may have to operate below optimal capacity or with increased risk (e.g., reduced fire protection), which could affect overall data center performance and reliability. |  | awaiting flow test data to asess, but moving forward under the assumption that the ACM water main site system of 8" WM pipes or the 24" WM in airport drive can provide the required cpacity |  | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:59
| SD054 | Site | Uncertainty and Non-compliance with Easement Regulations | The primary risk here involves potential legal and operational complications due to the uncertainty about the status of various water utility easements, both new and old, within the property. |  | - Legal and Regulatory Challenges: This could hinder ongoing development and maintenance activities. - Delays in Development: Ambiguity over easement rights and statuses can cause delays in construction and development projects as parties work to clarify and resolve easement issues. - Increased Costs: Potential for increased project costs due to legal fees, delays, and possible redesigns or rerouting of utilities to comply with established easement requirements. |  | Some easements for the new utilities have been recorded, but YCUA does not believe any of the R&D site easements have been. YCUA is waiting for a final set of record plans for the water mains and sanitary sewers in that the R&D area. YCUA is unaware of any of the easements over abandoned water or sanitary utilities were formally vacated. Easements for new water mains are defined by the Charter Township of Ypsilanti Engineering Standards and Design Specifications June 2020, "The easement width shall be the greater of the following: Twice the depth of bury plus the pipe diameter plus 2’ (rounded to the next largest full foot), or 15’." | dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:11
| SD055 | Fire/Life Safety | Inadequate Firefighting Water Supply | The primary risk is that existing fire hydrant flow data might not accurately represent current conditions, potentially leading to inadequate firefighting capabilities in the event of a fire. | - Reliance on Outdated Data: Depending on fire hydrant flow tests from 2014 and 2017 without more recent verification can be risky, especially if there have been any unrecorded changes in the water supply network or nearby developments that could affect water pressure and availability. - Assumed Stability in Site Conditions: YCUA's assumption that not much has changed on site might overlook minor changes that could significantly impact the hydraulic conditions of the water distribution system. | - Potential for Inadequate Emergency Response - Compliance Issues - Delayed Project Approval | Conduct Current Flow Tests and Possible Enhance On-Site Water Supply | Fire hydrant flow test from 2014 and 2017 in the vicinity of Project L were obtained from YCUA. YCUA indicates that they feel these Fire hydrant Flow tests are still valid given that not much has changed on site. additional hydrant flow test will be scheudled through YCUA. |  | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:59
| SD057 | Civil | Potential Infrastructure Failure | The primary risk is the potential for failure or inadequate performance of the water main, especially given its age and the lack of recent inspection data. This risk is exacerbated if the water main's condition has deteriorated without detection. | - Aging Infrastructure - Lack of Recent Inspections | - Water Supply Disruptions - Safety and Compliance Issues | Detailed Inspection and Condition Assessment, Infrastructure Replacement Planning, Stakeholder communication to manage expectations in preparing for potential disruptions | closed - The 24" water main along Airport Drive was installed during the late 1980s. No recent inspection data. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 12:59
| SD059 | Civil | Risk of Water Supply Interruption | The primary risk is the potential interruption in water supply due to a failure in the primary water service. Even though there is a redundant loop, the effectiveness and integration of this redundancy in preventing service interruption during a catastrophic event might be uncertain. | - Dependency on External Water Main Systems - Potential for Simultaneous Main Failures (The facility’s dependency on the external water main systems, particularly the 24" main along Airport Drive and the 36" main west of the project, can be a vulnerability if these mains are compromised simultaneously or if the redundancy does not function as intended.) | - Operational Downtime - Increased Costs - Safety and Compliance Issues | - Verification of Redundant System Functionality - Expand Water Storage Capacity - Stakeholder Coordination | Existing site water lines create a redundant loop as required by YCUA for Fire protection, connected to a 24" water main along Airport Drive and 36" water main west of the project site. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com, jamison.caldwell@smithgroup.com, Rob Teifer | In Control | 1 | 3 | 3 | P1 | 3 | 150000 |  |  |  |  | 2024-05-31 12:57
| SD061 | Civil | Disruption of Sewer Services | The primary risk is the potential disruption of sewer services to existing buildings during the utility relocation process. This could affect normal operations and sanitary conditions within those buildings. | - Utility Relocation Needs and Complex Coordination Requirements | - Service Interruptions - Increased Costs and Delays - Potential for System Failures | - Use of Temporary Solutions and Detailed Planning and Coordination | ACM has indicated that it is not a problem to move sewer utilities, as we identify which utilities need to be moved we should coordinate with ACM any requirements to maintain services to existing buidlings if impacted. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 12:57
| SD062 | External | Regulatory Compliance Uncertainty ( Land is leased or owned by the (UM)) | The primary risk involves uncertainty in regulatory compliance, which depends on whether the land is leased or owned by the (UM), as different standards may apply in either scenario. This could lead to planning and design adjustments later in the project lifecycle. | - Land Ownership Ambiguity: creates uncertainty about which local or UM-specific regulations apply - Preliminary Engagement Decision: The decision to delay engagement with Washtenaw County until the land ownership status is clarified adds to the regulatory compliance uncertainty. This decision seems to stem from a strategic choice to avoid premature or potentially unnecessary meetings. | - Planning delays: could postpone receiving crucial guidance on compliance - Potential for Redesign: design based on "One" Set of standards - Increasing project Costs | Plan is to evaluate the site assuming we would need to meet WCWRCO standards, as (from what we understand) they are more stringent than the EGLE requirements. This will allow us to identify any challenges we may have in meeting stormwater managmeent requirements and then if we later determine that those standrds are not governing we can adjust to EGLE requirements or have built in addtional capacity/resilience. (currently designing to stricter standards) | 3/5/24 SO Comment: 3.1..not sure if such a meeting is needed at this time with Wa. Co. Why meet with them until we know if this will be leased land or UM land. If leased, I would assume that the project would need to meet any local ordinance, whether that is the Washtenaw County standard (or Wayne County or Township) or not is TBD, based on the Township and/or County ordinance where the project is located. If the project land is owned by UM, the project needs to meet U-M's EGLE issued sw permit. The project can exceed our permit if desired. Also, if there are new connections to a County drain or a storm sewer system where there is not a current tap, we may have to meet others requirements. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD063 | External | Regulatory Compliance Challenges (location-specific requirements) | The risk involves potential challenges in meeting stormwater management requirements, especially if regulatory bodies have location-specific requirements or if there is a misunderstanding about how these requirements apply to the project's specific location. | - Misunderstandings or Lack of Clarity:The comment suggests a potential lack of clarity or misunderstanding about whether and how the project’s location might impact regulatory reviews, particularly concerning stormwater management practices. - Location at the Downstream Zone: The project’s location at the downstream end of the watershed may subject it to specific regulatory considerations that differ from other areas, potentially due to increased sensitivity or cumulative impact considerations. - Varied Regulatory Interpretations: Differing interpretations or applications of regulatory standards based on the project's proximity to county borders and its position relative to the watershed. | - Regulation delays, increased costs, design revisions, compliance risks | ACM suggested the Project L team engage RACER/EGLE to understand the stormwater management strategy that is preferred at the site, as it might be different than most site developments with respect to dentention and release of stormwater to the public infrastructure. Direct release of stormwater to the public infrastructure could be the preferred approach versus holding on site and controlling the rate of release. | 3/5/24 SO Comment: 3.2. Can't speak for the county but their permit requirements are not expected to be viewed differently. What difference does it being downstream near the border with another county have to do with anything? I do understand that Ann Arbor has sometimes waived requirements when a site is close to an outfall to a surface water (with the understanding that it may be better to get site water out of the system faster to free up capacity). Not sure project location has any impact here. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD064 | Civil | Non-compliance with Environmental Regulations (environmental regulations regarding stormwater infiltration) | The primary risk is the inability to comply with standard environmental regulations regarding stormwater infiltration due to site-specific challenges, namely soil contamination and unfavorable soil composition (clayey soils). This could lead to regulatory and environmental compliance issues. | - Site Contamination, Clayey Soils, Regulatory Complexity (overlapping jurisdictional regulations (Washtenaw County, Wayne County, Township, or UM rules) adds complexity to determining the appropriate stormwater management strategy.) | - Implementation of Alternative Stormwater Solutions - Increased Project Costs and Complexity - Potential Delays in Project Timelines | The project currently assumes that the WRC guideline of infiltration cannot be met (due to both site contamination and clayey soils), so additional detention will be provided to offset it. | 3/5/24 SO Comment: 3.3. EHS recommends no infiltration, only detention given the site is contaminated. The project can't exacerbate existing contamination. The project cant flush stormwater through existing soil contamination, or impact any existing groundwater contamination. Absolutely, no infiltration. If having to meet WCWRC rules, they have a caveat of 120% 100yr detention (I think) when you can’t infiltrate due to clay soils or contamination. They’d need to verify this, and also verify if the Washtenaw County rules could be applicable for this site, or is this subject to Wayne County rules or Township rules (if not UM rules). | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD065 | External | Misalignment in Regulatory Understanding and Compliance (misalignment between county-level understanding and enforcement of state-level environmental guidelines) | The primary risk is a potential disconnect or misalignment between county-level understanding and enforcement of state-level environmental guidelines (EGLE requirements), particularly concerning stormwater management in a contaminated section of the site. This misalignment could affect how stormwater management strategies are implemented and reviewed. | - Varied Levels of Contamination - Uncertainty about whether local authorities (WRC) are fully aware of or understand the specific EGLE requirements - Comment suggests a reluctance to engage the county (WRC) prematurely, based on an assumption that it might not be necessary | - Compliance challenges - Increased cost and project delays | Comprehensive Environmental Assessments, and Proactive Regulatory Engagement | 3/5/24 SO Comment: 3.4. See 3.1. We are not sure they would understand any EGLE requirements for the subject property at this time, but also, we do not feel that the County needs to be engaged just yet, if at all. Note - EHS recommends no infiltration. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD066 | Civil | Inadequate Stormwater Management Planning | Potential issues in planning and executing effective stormwater management strategies due to uncertainties about the storm sewer system's connectivity, the status of easements, and how stormwater is currently managed on site. | - Unclear Infrastructure Connectivity: Creates uncertainty about how effectively the site can manage stormwater, especially after development changes. - Easement Ambiguities: Easements that were drawn up but never formalized - Lack of Comprehensive Site Information: Not having clear, accessible, and comprehensive information about current easements, stormwater flow patterns, and connections to any county drains or public systems leads to gaps in planning. | - Project Delays - Increased Costs due to redesign of Stormwater systems, or constructing new connections to public stormwater infrastructure - Regulatory Compliance: Risk of being uncompliant - Potential Environmental Impact with chance of flooding or increased run-off | ACM indicates that the existing stormwater system was never connected to anything and changes can be made as necessary for the project L site. Easements were drawn but never formalized and can be revised as necessary. As we develop our storm water management we should coordinate with ACM to help them understand and plan for future site needs. | 3/5/24 SO Comment: 3.5..recommend starting with ACM. Also, are there any current easements? Does site stormwater flow to a County drain? Is there a storm system on-site? Where does it flow/connect to? Basically, we need to understand how stormwater leaves the site now, and how it might leave the site once developed. Some of this information (easements) should be available as part of the survey REO is conducting. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD067 | External | Regulatory and Compliance Confusion (ambiguities about the area of impact, ownership, and responsibility for environmental and infrastructural changes) | The primary risk involves potential misunderstandings or non-compliance with local regulations due to ambiguities about the area of impact, ownership, and responsibility for environmental and infrastructural changes, especially in relation to stormwater management. | Unclear Project Boundaries and Responsibilities: Uncertainty about whether the regulatory reviews will apply only to the disturbed area or the entire property Easement and Drainage Complications: The presence of existing easements, the need for new easements, and connections to county drainage systems can introduce additional regulatory requirements and complexities. This situation is further complicated if the land is not owned by the permit applicant (U of M), which might affect the rights and responsibilities regarding infrastructure modifications. Jurisdictional Overlap:The potential need to interface with multiple regulatory bodies (like WCWRC or other local entities) depending on where stormwater drains or connects, adds another layer of complexity, especially if new connections to storm systems are made. | Delays and increased Costs: Confusion over the scope of regulatory reviews, permit validity, and responsibilities can lead to delays in project approvals and increased costs due to potential redesigns or additional compliance measures. Compliance Risk: There is a risk of non-compliance with local regulations if the permit applications are not properly handled or if the project does not meet the specific requirements tied to the actual landowner's permissions and local stormwater management standards. Potential Legal Challenges: If UM is not the landowner and there are issues with permit legitimacy or easement rights, this could lead to legal disputes or challenges that might impede project progress. | - Clarify Land Ownership and Permitting Authority - Engage with WRC and other relevant regulatory bodies early in the planning process to clarify the scope of the project’s review and ensure all potential regulatory issues are addressed. | 3/5/24 SO Comment: 3.6 ? To answer this, I think we need to understand if this is going to be UM land or leased. Also, I think this could tie a little into item 3.5. If there are easements or there will need to be an easement, or if any of the stormwater drains to a county drain (or is newly connecting to a county drain) the project would have to work this out with WCWRC or other. Similarly, even if this is UM land, if we newly connect to another storm system, we could be at the mercy of the applicable entity. Would be helpful to understand current stormwater drainage, and proposed. | chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD068 | Electrical | HV substation secondary 15 kV gear | ACM ownership and management of the substation gear | The data center may have limited control over the quality and reliability of power distribution, as well as the priority given to maintenance and upgrades. | Operational Disruption - delays in upgrades Increased Cost | - Establishment of Service Level Agreements (SLAs) - Include backup power solutions or alternative sources in case of substation failure | Firm decision isn't determined to own gear in the yard. | andrew.varilone@smithgroup.com | At Risk | 3 | 3 | 9 | P3 | 3 | 600000 |  |  |  |  | 2024-05-22 09:22
| SD069 | Electrical | Inadequate Power Supply and Metering | The primary risk involves potential miscalculations or misunderstandings about the number and location of primary service meters needed, which could lead to inadequate power supply for the project or inefficient power distribution and monitoring. | Unclear Power Requirements and Lack of Coordination with Utility Provider | Delays in Project Completion, increase costs with possible need to modify meter setups after initial installation, and Operations | Detailed Power Demand Assessment, Engage closely with DTE Energy, Strategic Meter Placement Planning | Where and what quantity of DTE primary service meters will be needed? (no answer provided) | andrew.varilone@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:22
| SD070 | Electrical | Insufficient Documentation and Information Accessibility | The primary risk is the potential lack of comprehensive and accessible documentation on existing electrical infrastructure, which is crucial for planning, maintenance, and any future upgrades. | - Dependency on Multiple Sources for Documentation and Potential Gaps in Existing Documentation | Delays in Project Execution, Increased costs due to rework or modifications to design | PSW provided by DTE. Other drawings would come from ACM. Substation upgrade/Expansions | Are any drawings available of the existing transformers, secondary feeders, substation yard, and associated switchgear? | andrew.varilone@smithgroup.com | At Risk | 3 | 4 | 12 | P3 | 4 | 1600000 |  |  |  |  | 2024-05-22 09:22
| SD071 | Electrical | Inadequate Access to Critical Infrastructure Information | The main risk is the lack of detailed circuit maps for primary transmission lines, which can impede effective planning, risk assessment, and emergency response strategies for the substation and associated infrastructure. | Ownership and Confidentiality Issues that are preventing sharing the information, Was told this information will not be provided. . | Planning and Development Delays and will create challenges with coordination (coordination among various stakeholders such as utility companies, emergency services, and local government agencies ) | Unable to provide circuit maps, but the substation is fed from ITC owned 120kV lines Willow Run-Zebra and Scottsdale-Willow Run. Need to provide Load letter to confirm we have the capacity we need once project becomes public | Are drawings available which show the surrounding area served by the primary (high voltage) transmission lines serving the substation? | andrew.varilone@smithgroup.com | At Risk | 1 | 4 | 4 | P1 | 4 | 400000 |  |  |  |  | 2024-05-22 09:22
| SD075 | Electrical | Insufficient Electrical Infrastructure Capacity and Efficiency | The primary risk involves potential inadequacies in the substation's ability to handle projected loads efficiently and safely after upgrades, including issues related to fault current management, power factor correction, and additional transformer installation. | Uncertain Electrical Specifications and Existing Infrastructure Limitations | Cost associated with adding another Transformer | Plan for necessary upgrades and expansions carefully, ensuring that all new installations, like additional transformers, are fully integrated into the system design to handle expected loads and improve overall efficiency. | What will the maximum available fault current be at the transformer secondaries after the DTE transformers are upgraded? | andrew.varilone@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:22
| SD079 | Electrical | Non-Compliance with Utility Relaying Requirements | The primary risk involves potential non-compliance with the utility provider’s (DTE’s) relaying requirements. This non-compliance could occur if the specifics of the installed customer equipment (like generation units and large motors) necessitate additional requirements that are not initially addressed. | Varying Requirements Based on Equipment and the need for DTE’s Primary Services and Relay engineering team to review and approve customer one-lines (schematic diagrams of an electrical service) indicates a multi-step compliance process. This could lead to delays or revisions if the initial submissions do not meet DTE’s specific standards or if they fail to account for the unique aspects of the installed equipment. | Delays in Project Implementation, cost impacts due to adding additional relaying equipment, and redesign parts of the electrical system. | DTE’s standard industrial substation relaying requirements should apply. Requirements can vary depending on customer equipment such as generation, motors, etc. Primary Services and Relay engineering will need to review and approve customer onelines. | Does DTE have any specific relaying requirements in the switchgear above and beyond their typical requirements for primary services? | andrew.varilone@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:26
| SD081 | Electrical | Insufficient Electrical Infrastructure Capacity | The primary risk is that the existing switchgear may not have adequate capacity to meet the high power demands of an HPC data center, particularly if the 3000A bus rating is not confirmed to be sufficient for current and future loads. | Uncertainty and Assumptions about Existing Infrastructure and Adaptation of Brownfield Site | Potential for Overloading if HPC DC exceed the capacity of existing switchgear, increased cost for upgrades or replacements | Likely 3000A, to be verified - Verification and Testing, Load Analysis, capacity planning | What is the bus rating of the existing switchgear? | andrew.varilone@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:26
| SD082 | Electrical | Project Delays Due to Long Lead Times for Transformer Upgrades | The primary risk is potential delays in completing the project if the transformer upgrades, crucial for the operational capability of the HPC data center, are not completed in sync with the overall project timeline. | The projected 2-3 year timeframe for upgrading the transformers is attributed to the long lead times commonly associated with manufacturing and delivering such large and complex equipment. | Delay project completion, increased cost due to extended labor contracts, longer rental periods, and higher cost for materials | Likely 2-3 years based on equipment lead time. Note, this is very high-level and would be refined as a more detailed scope is developed. - Develop a more detailed and precise procurement plan for the transformers as soon as possible. This should include securing contracts that can fix prices and delivery schedules, potentially including penalties for late delivery to mitigate risks. (order transformers early and have it stored on or off-site) | What is the timeframe to upgrade three transformers to provide 110MVA? Lead time is risk, but low risk | andrew.varilone@smithgroup.com | At Risk | 2 | 4 | 8 | P3 | 4 | 800000 |  |  |  |  | 2024-05-22 09:29
| SD144 | Mechanical | Inappropriate Design and Environmental Controls | The primary risk is designing and constructing data hall spaces without appropriate environmental controls that meet the necessary clean room standards for the intended operations. | Lack of detailed understanding of the operational demands and the environmental sensitivity of the equipment to be housed in the data center. | Costly Redesigns and Retrofits, | typically in the range of ISO Class 8 or ISO Class 9 | Need level of clean room classification for server data hall spaces: ISO Clean room level 1-9. Which one is required? | Interiors | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-22 09:22
| SD173 | Fire/Life Safety | Potential for Inadequate Safety Measures During Tornado Events | The primary risk is the facility not having dedicated tornado shelter spaces, which could lead to insufficient protection for occupants during a tornado, especially in regions susceptible to such weather events. | The current building codes and (UM) requirements do not mandate tornado shelters, which may lead to their exclusion in the facility design. | Safety Concerns Cost impact if we need to add it later | Design and Construct Tornado Shelters | Per Laura: We asked about tornados in the CDR phase and there was no requirement. Per my research back in the CDR- Since 1950 there has been 21 total tornados in Washtenaw County with three F3 tornados, five F2 tornados, nine F1 tornados, and four F0 tornados. There were no F4 or F5 tornados which cause the serious damage. | Laura Holman | At Risk | 3 | 3 | 9 | P3 | 3 | 600000 |  |  |  |  | 2024-06-07 14:22
| SD174 | Technology | Delay in Utility Service Establishments (Fiber) | The primary risk is potential delays in the establishment of critical utility services, particularly fiber connectivity, which could impact the project timeline and operational readiness. | Pending Project Announcement and the need for coordination between the Owner’s IT services and fiber service providers is crucial. Delaying this coordination until after public announcement might result in delays in starting the engineering phase for fiber installation. | Potential Project Delays and could impact cost by expediting work needed later or incorporating temporary solutions. | Comment on fiber timeline:UM ITS has started initial communications with their fiber service provider. Since the project has not been made public UM ITS will engage the fiber service provider when this project is publicly announced. Little impact at this time. Believe that the UM fiber and their service provider will engage in early DD phase to begin engineering. | Risk until we can identify and confirm UM Ownership | tim.johnson@i2techdesign.net | At Risk | 3 | 2 | 6 | P2 | 2 | 200000 |  |  |  |  | 2024-06-07 14:22
| SD175 | Technology | Insufficient Utility Infrastructure to Support Project Needs (Fiber Upgrades) | The primary risk involves the potential inadequacy of existing utility infrastructure (in this case, fiber) to meet the project requirements, necessitating significant upgrades. | The current fiber connections are not in close proximity to the Project L property boundaries, requiring extensive upgrades, including the creation of an approximately 8000 ft redundant A-B fiber underground pathway. Additionally, inability to provide a cost estimate until the fiber service provider is fully engaged, and path engineering is completed adds uncertainty to budgeting and project planning. | Cost impact: The cost of the addition of the fiber from the service providers interconnect vaults to the Project L property boundary will not be available until service provider is engaged and path engineering is completed. | Unknown—however, we need to coordinate the fiber UG infrastructure in the site plan with other utilities as soon as possible. |  | tim.johnson@i2techdesign.net | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-06-04 09:00
| SD176 | Technology | Temporary Services | Temporary internet and WIFI has not been assessed at this time. | Deferred Assessment and it still being early in design phase | it is possible that comprehensive needs for temporary utilities have not yet been fully identified or considered, leading to gaps in immediate planning and setup. | Very early in design will be looked at later in the design progess (DD Phase) |  | tim.johnson@i2techdesign.net | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-06-04 09:00
| SD180 | External | Is the Township Permitting period known? Is it a complex permitting process? If so, please note any specific requirements under comments. | Permitting Period will likely require many reviews prior to approval and the full impact of timeframe is only assumed currently. | only 1x month meetings to do reviews (#job creation and esthetics) Project not currently public | Schedule, cost, Scope, denies approval | Built this into the design fee to assume additional time. Build into schedule. | Process is developed and shared with UM to manage expectations | dino.lekas@smithgroup.com | At Risk | 2 | 3 | 6 | P2 | 3 | 300000 |  |  |  |  | 2024-06-07 14:22
| SD181 | External | Are there AHJ site wide landscaping and planting requirements, including any streetscape planting for frontage? | [5 empty] | dino.lekas@smithgroup.com | Closed |  |  | 0 | [7 empty] | 2024-05-22 08:59
| SD182 | External | Are there any AHJ planning requirements or restrictions for street frontage or façade treatment? | Dino/ Chris D. |  |  |  |  | dino.lekas@smithgroup.com | Closed |  |  | 0 | [7 empty] | 2024-05-22 08:59
| SD183 | Site | Will the existing landowner clear the site of contaminants existing services, structures, species as this is understood to be done as part of a separate budget. Can we confirm? | Utility yard position is the location of the contaminated area and all other areas are clean. | Caused Brownfield Manufacturer | Requires more clean fill, cost | Haul off and bring in all clean fill. (confirm cost covered with KAS) Unlikely this applies in other areas of the site as its been determined as clean. | UM and ACM are discussing and coming to an agreement of what is existing. Geotech report will be completed and UM RACER Trust (entity from GM bankruptcy to manage their own land report) | Brandon Stanley, dino.lekas@smithgroup.com | In Control | 1 | 4 | 4 | P1 | 4 | 400000 |  |  |  |  | 2024-05-31 13:29
| SD184 | Site | Will this site likely require cut/fill/retaining walls due to the topography; or piling due to aluvial soils? | Cut and fill yes, retaining wall at loading dock |  |  |  |  | Laura Holman | Closed |  |  | 0 | [7 empty] | 2024-05-22 08:59
| SD185 | Site | Are there any other unique existing site conditions of concern which may impact cost, schedule, safety and logistics around future fit-out or build. | Possibility of unsuitable soils on site that wasn't anticipated | No Geotech report | Cost, scope, | Haul off and Bring in clean fill |  | dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD186 | Site | Has soil contaminants (if any) been identified? If so, what is the approximate volumes and treatment timelines? | no geotech yet - phase one study done in 2017 |  |  |  |  | Laura Holman | Closed |  |  | 0 | [7 empty] | 2024-05-22 08:59
| SD187 | Technology | Rack Technology | Rack Technology may change and cabinet counts may reduce with additional added PDUs to the aisles that will take up significant space | New information for 100MW side associated with expanded trench lines. PDUs needing to be added to the floor space. | Change dynamic of floor plan, scope, cost, schedule (Impacts hot/cold aisles arrangements) but will reduce number of cabinets. | Coordination of space needs to reduce impacts to other scope |  | tim.johnson@i2techdesign.net | At Risk | 4 | 3 | 12 | P3 | 3 | 1200000 |  |  |  |  | 2024-06-04 09:00
| SD188 | Security | Security | Security vulnerabilities: Without a thorough security review during the Critical Design Review (CDR) phase, the project is at risk of having undetected security vulnerabilities. Project delays: New comments and issues identified at a later stage can lead to significant project delays as they need to be addressed. Incomplete design: Lack of complete inputs from layouts, POR (Point of Reference), etc., can result in an incomplete or flawed design. | Inadequate review process: The primary cause is the insufficient security review during the CDR phase. This oversight might be due to resource constraints, scheduling issues, or a lack of awareness of the importance of this step. Missing inputs: Another cause is the absence of complete inputs from various sources such as layouts and POR, leading to gaps in the design process. This might be due to poor communication, inadequate documentation, or incomplete data collection. | Increased costs: Addressing security issues and design flaws at a later stage can be more expensive and time-consuming than if they were caught earlier. |  |  | Laura Holman | At Risk | 3 | 3 | 9 | P3 | 3 | 600000 |  |  |  |  | 2024-05-31 08:08
| SD189 | External | Client changes to program requirements for offices and occupancy | Scope creep: Frequent or significant changes to program requirements can lead to scope creep, where the project expands beyond its original boundaries. Resource strain: Adjustments to requirements can put a strain on resources, including time, budget, and personnel. Misalignment: There is a risk of misalignment between the client's expectations and the project's capabilities, leading to potential dissatisfaction. | Client-driven changes: The cause of this issue is the client's decision to alter the program requirements for offices and occupancy. Changing needs or priorities: These changes may stem from evolving business needs, market conditions, or a reevaluation of space and occupancy needs. Inadequate initial planning: Another possible cause could be insufficient initial planning or understanding of the client's needs, leading to adjustments during the project. | Project delays: Implementing changes can delay the project timeline as adjustments need to be made to accommodate new requirements. Increased costs: Changes to program requirements often lead to increased costs due to additional work, materials, or modifications. Design alterations: The project design may need significant revisions, which can impact the overall aesthetic and functional aspects of the offices and occupancy plans. Stakeholder dissatisfaction: Frequent changes can lead to frustration among stakeholders, including the project team and end users, due to the uncertainty and instability introduced into the project. |  |  | Laura Holman | At Risk | 3 | 3 | 9 | P3 | 3 | 600000 |  |  |  |  | 2024-05-31 08:08
| SD190 | Security | Revised DOE security requirements, see above, | [5 empty] | Laura Holman | Closed |  |  | 0 | [7 empty] | 2024-05-31 07:56
| SD191 | External | ACM Masterplan | ACM requirements for master plan are not completely defined and its impact to the UM site | No having the ACM Master plan and power needs are promised "Verbally" only and the risk of other Data Center 60 MW anticipated | Power and water usage on site. | Substation expansion and/or upgrade Water: Previous user was utilizing 3m gallons a day and is above was needed and should not be a risk. | Benchmark for water and sewer is, letter was sent every 6 months to hold needs as a possible mitigation | andrew.varilone@smithgroup.com, chris.devick@smithgroup.com, dino.lekas@smithgroup.com | Closed |  |  | 0 |  |  | #NO MATCH |  |  |  |  | 2024-05-31 13:29
| SD192 | External | More DOE Requirements from LANL | Increased requirements: The risk that the (LANL) may ask for additional Department of Energy (DOE) requirements as the design phase progresses. Financing challenges: The need for "Financing Cost" to meet DOE standards introduces financial risks, including securing adequate funding and managing budget constraints. Project delays: The incorporation of additional DOE requirements and financing considerations can delay project timelines.. | Evolving project scope: As the project advances into further design, new requirements and standards from LANL and DOE might emerge that were not initially considered. Regulatory compliance: The need to comply with DOE standards necessitates adjustments to the project's financial planning and design to ensure adherence. Detailed design insights: Deeper design phases often reveal additional regulatory and financial requirements that were not apparent in earlier stages. | Increased project costs: Additional DOE requirements and the need to meet "Financing Cost" standards will likely increase the overall project budget. Extended timelines: The need to integrate new requirements and secure financing can lead to project delays, potentially affecting the delivery schedule. Complexity in design: Incorporating additional DOE requirements can add complexity to the design process, requiring more resources and expertise. Stakeholder pressure: Managing increased costs and extended timelines can put pressure on project stakeholders, including project managers, financial planners, and regulatory compliance teams. |  |  | mhankewycz@m2hprotection.com | At Risk | 3 | 3 | 9 | P3 | 3 | 600000 |  |  |  |  | 2024-05-31 08:14
| SD194 | Security | Revisions to Security Areas | Getting these revisions into the 100% design that would require movement of data hall to make room for security | Revisions to security areas | Cost, scope, Schedule | Present a plan with how we will address the new requirements. 100% plans won't have the request in time for SD. |  | Laura Holman | At Risk | 3 | 3 | 9 | P3 | 3 | 600000 |  |  |  |  | 2024-05-31 08:14
| SD195 | External | Tornado Risk | Shelter built-in to the design within the facility | Not in scope and not required by UM, DOE may require it. Likely under leasing situation. | Cost, scope |  |  | Marty Sterr | At Risk | 3 | 2 | 6 | P2 | 2 | 200000 |  |  |  |  | 2024-05-31 08:15
| SD196 | Site | Site Utilities in Easments | If the existing utilities beneath building footprint are not in use, then they be abandoned in place. Otherwise there is a risk of relocation requirements if they are found live. | Unknown if they are live or "not in use". | Remove cost is accounted for based on it was abandoned and not live. If they are active, then we would have to relocate them. Easements redone and legal impacts | Easements will need to be redone and relocate active lines. ACM and Utilities to determine next steps to determine what is existing. | I have other item(s) to add to the risk register. This is coming to light as our survey is nearing completion. There are utilities that cross the site, many with easements. We had received drawings from previous design work at the site where many of the utilities were either removed or abandoned (there are symbols on the drawing which imply their removal or abandonment but it is not clear which). I just had a discussion with our surveyor as these utilities are still showing in the document our survey team is developing. He said he cannot find record of whether the utilities have been removed or abandoned; or if they are still active. It is something that will require further investigation. Also, the project will have to work to modify the easements associated with these utilities that cross the site. We'll try to get more info on the utilities and the easement changes will likely require attorney work to remedy. I don't think it's insurmountable, will mostly take time to untangle. | dino.lekas@smithgroup.com | At Risk | 2 | 3 | 6 | P2 | 3 | 300000 |  |  |  |  | 2024-05-31 13:11